## Slide 2
Inside ComEd’s Operational Analysis with Distribution Automation
Leonardo Lopez | ComEd | Engineer
Erin Sarver | ComEd | General Engineer
March 27, 2025

## Slide 3: Agenda
ComEd Overview
ComEd Distribution Automation (DA)
Operational Analysis Topics
                DA Event Logs
      Fault Locates
Operational Analysis Look Ahead
Q&A
Notes: Erin

## Slide 4
Notes: Erin

## Slide 5
Distribution Center
345kV
138kV
34kV
12kV
4/12kV
Sectionalizer
Recloser
Line Sensor
Distribution Automation (DA) devices are specifically located on 34kV, 12kV, and 4kV lines. DA protects customers from disturbances on the distribution system and redirects the power system to automatically restore customers in response to an event.
Notes: Erin

## Slide 6
DA System Impact:
~9,000 reclosers
~1,200 sectionalizers
In 2024, there were:
Snapshot: Distribution Automation
 | # of Scheme operations | # of DA operations | Avoided Customer Interruptions (ACI)
4kV | 18 | 32 | 6,265
12kV | 2,243 | 6,632 | 1,632,500
34kV | 355 | 1,566 | 606,000
Total | 2,616 | 8,230 | 2,244,765
56% of circuits
84% of customers
Notes: Erin

## Slide 7
Identify – For any event involving DA devices that results in system reconfiguration on the 4kV, 12kV, and 34kV, an event record needs to be generated and stored in a central repository.
Analyze – The DA Engineering team then analyzes each event and validates the proper operation of automated devices. For each event, the number of Avoided Customers Interrupted (ACI) is calculated. ACI is the number of customers that would have otherwise experienced an outage were DA not installed. ACI is crucial in telling the story of DA’s impact on system reliability and in planning for future installation of additional devices.
Act – Corrective action can be taken immediately if the event analysis indicates a mis-operation of DA devices. Event analysis helps us better understand our system, leading to improved overall system performance and reliability.
DA Logs – Overview
 | Circuit | kV | Event Date | Hour | Minute | ACI | Missed ACI
 | A123 | 4kV | 1/1/25 | 01 | 23 |  | 
 | B345 | 12kV | 1/1/25 | 12 | 05 |  | 
 | C678 | 12kV | 1/2/25 | 04 | 47 |  | 
 | A123 | 4kV | 1/2/25 | 16 | 33 |  | 
 | D910 | 12kV | 1/3/25 | 21 | 54 |  | 
 | L1111 | 34kV | 1/3/25 | 22 | 19 |  | 
Notes: Erin

## Slide 8
Outage Tickets:
Customer calls
SCADA
AMI meters
This method will not capture events with no sustained customer outages
Device Operation Logs:
DA device operations (open/close)
An event is logged if a DA device opens and stays open for 5 minutes
This method will not capture events with no DA device operations
DA Logs – Identifying Events
Event records are generated by two methods:
Both methods are required to capture all events involving DA on the distribution system. These events are then stored in a central repository for review by the DA Engineers.
outage tickets
device operations
EVENT RECORDS
Notes: Erin

## Slide 9
For each event, DA needs to determine the following:
DA Logs – Analyzing Events
ACI = the number of customers that were restored or retained power
Missed ACI = the number of customers that were not restored or lost power due to incorrect DA device operations
Device Count = the number of DA devices that were intended to operate
Mis-Op Device Count = the number of DA devices that operated incorrectly
LEGEND
Device Rate =
Scheme Rate =
device count – mis-op device count
device count
________________________
total # of scheme operations
________________________
# of correct scheme operations
Notes: Erin

## Slide 10: DA Logs – Calculating ACI
Station Breaker OPEN on overcurrent
Station Breaker CLOSE
Station Breaker OPEN on overcurrent
Station Breaker CLOSE
Station Breaker OPEN on overcurrent
DA Device 1 OPEN on loss of voltage
DA Device 3 OPEN on loss of voltage
DA Device 4 OPEN on loss of voltage
DA Device 2 CLOSE
DA Device 5 CLOSE
DA Device 4 CLOSE
Device reclosed
Device Rate: 5/5
Scheme Rate: 1/1
ACI = 1,500
Missed ACI = 0
Device Count = 5
Mis-Op Device Count = 0
Sequence of Operations:
LEGEND
Notes: Erin

## Slide 11: DA Logs – Identifying Mis-Operations
If the final configuration is not as expected, thorough investigation by the engineering team is needed to determine if a mis-operation occurred.
Several factors could contribute to a mis-operation, including communication interruptions, equipment failures, or improper settings.
Additionally, the team must look out for any intentional cause of a DA device to not operate (i.e., Hot-Line Tag, auto-operation disabled, etc.). This would usually be a condition placed by the operator and would not be considered a mis-operation.
ACI = 1,000
Missed ACI = 500
Device Count = 5
Mis-Op Device Count = 1
Device failed to close
Device Rate: 4/5
Scheme Rate: 0/1
LEGEND
Notes: Erin

## Slide 12: DA Logs – Improvements and Automation
First Iteration
Consolidate data sources to be shown in one location: SCADA, PI, Powerbase, CEGIS, OMS Outage Tickets
Create a generic output describing the event that is easily editable
Second Iteration
Create a digital model of the circuit using DA device information such as their feeder, normal positions, and their upstream devices
Analyze the event using PI and SCADA data such as device operations, overcurrent targets, and loss of voltage targets
Making the “generic output” as detailed and accurate as possible
Estimated Time Savings of 600 hours per year
for the DA Engineering Team
RESULT: Automatic calculation of ACI and number of devices that operated, filtering out possible mis-operation events for now.
Notes: Leo

## Slide 13
Fault locating is performed to help narrow down where a fault occurred on a line. ComEd performs a fault locate study on any 34kV event with unknown cause, even those caused by a transient fault. This enables teams to quickly identify and address damage-inducing faults. This capability not only streamlines repair efforts but also reduces outage time for customers with sustained interruptions.
Method: Short Circuit Analysis
Inputs:
Thevenin value of the bus
Pre-fault voltage
Max fault current
Fault type (LL, LG, LLG, LLL)
Fault locate
narrows patrol zone to
1-2 miles
Real
System
Impact
34kV line with
30+ miles
of overhead exposure
DA device fault targets narrow patrol zone to
~10 miles
narrowing in
Output:
Distance of the fault from the bus
Fault Locates – Overview
Notes: Leo

## Slide 14
CAPE
Used to obtain the Thevenin values of bus
Crossbow & Synchrowave
Used to gather fault inputs from the station such as fault current, fault type, and pre-fault voltage
DA Devices
Used to gather fault inputs from the DA devices such as fault current and fault type
CYME
Takes data from the sources above as inputs and performs the locate
Fault Locates – Programs and Data Sources
Notes: Leo

## Slide 15
Output of short circuit analysis: Distance of the fault from the bus
If the circuit branches in two directions, it is possible for multiple sections to be the same distance from the station resulting in multiple potential fault zones.
To overcome this obstacle, DA device fault targets can be used to help identify the correct fault zone.
Fault Locates – Results
Substation
DA device
Potential fault zone
LEGEND
Targets for Over Current
Notes: Leo

## Slide 16
First Iteration
Utilizing Cyme Python module that allows fault locates to be run via a script
Code allows data to be input from outside sources such as the Thevenin impedances from Cape
Outputs potential fault zones overlayed on a geographical map of the line
Second Iteration
Connect the script to more data sources
Compare potential fault zones with fault targets from DA devices
Set up a system to provide fault data to the script directly
RESULT: One-click process to replace a multi-step fault locate process,
thereby further speeding up the time in which crews can respond to an event.
Estimated Time Savings of 240 hours per year
for the DA Engineering Team
Fault Locates – Improvements and Automation
Notes: Leo

## Slide 17
Operational Analysis Look Ahead
Auto-identify and complete non-mis-operation events
Pulling the information needed to analyze suspected mis-operations
Create script for analyzing suspected mis-operations
DA
Logs
Auto-populate fault type and fault current into script
Create script to continuously identify and perform fault locates in real time
Set up a system for sharing and storing information from these locates
Fault Locates
now
more automation
more time savings
future
Notes: Leo

## Slide 18
Leonardo Lopez
  ComEd
  Engineer
  Leonardo.Lopez@ComEd.com
Erin Sarver
ComEd
General Engineer
Erin.Sarver@ComEd.com
Thank You